## Slide 1: Level 2 DG Studies – CMP Policy Change (Effective July 16, 2025)
  CMP will no longer include minimum loading on the circuit for Level 2 DG Thermal Analysis – for all new studies starting after July 16, 2025
  This is due to real-time operational concerns that CMP is seeing across the system.
  Level 2 DG Studies are completed as a snapshot in time, using min load at that time, however, minimum load is decreasing in some areas due to:
        Total aggregate generation (all Levels) reducing the minimum load on a circuit/substation transformer
        Businesses closing, downsizing, or converting to more energy efficient practices
        Existing Risk: identified multiple substation transformers currently at risk of exceeding 100% transformer nameplate in reverse direction – due to decrease in minimum load
  Policy change aligns with neighboring New England and New York Utilities